- Hydropower Sizes

| Size | Power Output | Typical Use |
| --- | --- | --- |
| Large | >10MW | Usually part of a large grid. |
| Small | 1MW-10MW | Usually grid intertied. (up to 50MW in Canada[1]) |
| Mini | 100kW-1,000kW | Community and industry. Often grid intertied. |
| Micro | 1kW-100kW | Small community, small industry, rural high energy consuming household. Usually off-grid. |
| Pico | <1kW | Radio tower, low energy consuming household, charging station. Almost always off grid. |

Please note that these are averages, many different communities classify hydropower somewhat differently.

- Equation

The amount of energy released by lowering an object of mass by a height in a gravitational field is[2]:

where is the acceleration due to gravity.

Converting these units, a common field equation to measure the maximum power available in a moving body of water is:

Where:

- Pmax=Maximum Power Available (kW)

- Qmax=Flow (Volume/time)

- Hmax=Head (Vertical drop in ft)

- emax=Efficiency of the turbine (use a value of 1 for max power available)

- K=Unit conversion factor (see table below for some common values)

| For Q measured in | K is equal to |
| --- | --- |
| ft3/min | 708 (ft4)/(min*kW) |
| ft3/sec (CFS) | 11.8 (ft4)/(sec*kW) |
| l/sec | 102 (l*ft)/(sec*kW) |
| gal/min (GPM) | 5302 (gal*ft)/(min*kW) |

To find the actual power you will get from that moving body of water, calculate Pnet with the following changes made.

Where:

- Pnet=The net power extracted from the river, not including loss in delivery from power station to load (kW)

- Qnet=Flow (Volume/time) - Only take a portion of the max flow (%take). For delicate streams this may be a small percentage of the total flow.

  - Qnet=Qmax*%take

- Hnet=Head (Vertical drop in ft) - This is the actual head that you have available due to losses from friction. Calculate friction loss using tables based on the materials you use for diversion (e.g. PVC).

  - Determine equivalent length of pipe by adding actual length of pipe and equivalent lengths of fittings based on tables using pipe size.

  - Find Frictional Pressure Loss Ratio (FPL) coefficient in ftloss/ftpipe based upon flow rate and pipe size

  - calculate Hloss=equivalent length of pipe * FPL

Hnet=Hmax-Hloss

- enet=Efficiency of the turbine - Always between 0 and 1, usually between .5 and .9 depending on the turbine type and flow rate. A value of 0.78 is a good guess for modern turbines in average conditions.

- K=Unit conversion factor (see table above for some common values)

Note that these equations are static in time. You must run these equations for with a resolution high enough to cover periods of variation (e.g. monthly river data).

Further Resources:

- http://www.appropedia.org/Microhydro - This document is an excerpt from this link.

- http://www.microhydropower.net/ Check out their case studies (under the resources pull down window). Avoid their theory sections.

- http://www.homepower.com/basics/hydro/ Great basics of microhydro from Home Power magazine.

- http://www.retscreen.net/download.php/ang/109/0/Textbook_Hydro.pdf Awesome textbook on small hydropower installations. They also have data, case studies and tools available for doing project analysis. See http://www.retscreen.net/ang/g_small.php for much more.

- wikipedia:Hydroelectric power and wikipedia:micro hydro More information from wikipedia.

- Micro Hydro A visual directory of microhydro resources from the Renewable Energy Directory.

- DC Micro Hydro Examples and AC Micro Hydro Examples A great resource with pictures, statistics, and an overview of the necessary elements of micro hydro.

- CD3WD - Helping the 3rd World to help itself A website which gathers articles from NGO's and other organizations and compiles them on CD's . The images of that CD's can be downloaded through their website. The CD's that have identified by me to contain information about hydro power are cd3wd407 and cd3wd430.

- Power versus Pipe Diameter Live spreadsheet graph of Power versus Pipe Diameter for Various Flows (0 to 150GPM). Customizable amount of run and fittings.

- Ashden Awards Awesome case studies with video.